# NOISEBLOCK™ BARRIER WALL, Model B, Air-Cooled Chillers, SPECIFICATION

(Barrier Wall + Access Door)

- General

  - Acoustic barrier wall panels shall be insulated, double-wall construction and shall be provided as indicated on drawings by a recognized manufacturer with published standards of construction and technical performance. The manufacturer shall have produced a standard factory fabricated, modular panel system and components for at least 10 years.  Performance of the fabricated and installed system shall conform to all specifications listed herein.

  - The “Model B” barrier wall system is designed with clearances between acoustic wall and chiller as dictated by the chiller manufacturer.

- Materials

  - Acoustical Metal Panels

    - All barrier panels and their components shall be factory fabricated, sectional, and all metal-clad modular designed for easy and accurate field assembly. The panels and components shall not be susceptible to damage due to extended exposure to vibration, air temperature or humidity with the passage of time.

## Panel Construction

    - All panels shall be (4) inches thick, as noted on drawings, with a solid exterior shell and a perforated interior shell; all material to be galvanized steel, Type G90. The panels shall be connected together by means of a tongue and groove connection and held together rigidly by the use of sheet metal screws.  H-joiners or snap-lock connections are not permitted.

    - The panel shells, framing members, and internal reinforcements shall be spot welded together to form a metal-sheathed panel of sufficient strength for maximum operating loads specified in the structural performance section of these specifications.

    - The outer galvanized steel shell thickness shall be 16 ga. minimum and the inner galvanized steel shell shall be 22-gauge minimum thickness.

    - Where perforated materials are indicated, all perforations shall be 1/8" dia. holes on 3/32" staggered centers and shall result in an open area of no less than 23 percent.

    - All panel internal reinforcing members shall be minimum 18 ga. galvanized steel, type G90.

    - Each panel shall be filled with sound absorbing materials that are inert, mildew-resistant, vermin proof, and incombustible and inherently suitable for wet/dry, freeze/thaw cycles.  Use of a moisture barrier is not permitted.

  - Panel Components

    - All accessory trim items shall be of 18 ga. minimum galvanized steel, type G90 and shall be furnished in factory standard lengths to be field cut to specified dimensions. Location and quantity of sheet metal screws and trim requirements shall be in accordance with the barrier wall system manufacturer’s installation details.

    - All external panel connections, trim items, accessories, panel interfaces and other sections as noted on the drawings.

- Structural Performance

  - Any special external panel loading conditions including wind, snow, and equipment shall be provided for as per specifications.  Panel manufacturer shall provide and note on the submittal drawings the reaction forces at each column base plate, due to the site loading conditions.

  - The barrier wall system manufacturer shall provide a copy of all structural calculations with barrier wall system submittal drawings to be used by the engineer of record for designing the foundation and foundation anchors.

  - The structural members shall be designed as a field bolt-together system.  All holes in column webs, backer angles and base plates shall be factory drilled.  All nuts, bolts and washers to be supplied by barrier wall system manufacturer.  Field welding of structural components is not permitted.

  - Columns and base plates shall be supplied as factory-welded assemblies by the barrier wall system manufacturer.

  - Under the indicated loading conditions, the entire barrier panel system shall be self-supporting and/or will be supported as per the specifications. The installer shall erect all structural members in strict accordance with the manufacturer’s piece-marked installation drawings and details.

  - Under the above loading conditions, the assembled acoustical structure shall not exhibit any panel joint deflection in excess of L/240, where L is the unsupported span length of any panel section in the erected structure.

- Acoustical Performance

  - The manufacturer shall provide certified independent test data indicating sound absorption and transmission loss characteristics of the panel assembly.  Test data must be obtained through independent tests conducted in a NVLAP accredited laboratory in accordance with ASTM E90, Standard Recommended Practice for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and ASTM C423, Standard Method of Test for Sound Absorption of Acoustic Materials in Reverberant Rooms.

  - Panels shall exhibit a minimum STC 40 and NRC 1.0

- Doors

  - Single or double leaf access doors to have heavy duty hinges, panic/passage hardware and seals to prevent sound leakage.  If door windows are included, windows shall be double-pane, wire-reinforced or tempered.

- Submittals

  - The barrier wall system manufacturer shall provide a copy of all structural calculations with barrier wall system submittal drawings to be used by the engineer of record for designing the foundation and foundation anchors.

  - Any special external panel loading conditions including wind, snow, and equipment shall be provided for as per specifications.  Panel manufacturer shall provide and note on the submittal drawings the reaction forces at each column base plate, due to the site loading conditions.

- Installation Drawings

  - The barrier wall system manufacturer shall provide complete piece marked installation drawings corresponding to all factory piece-marked barrier wall system components.

- Manufacturer

  - All materials shall be provided by Kinetics Noise Control, Inc., trade name NOISEBLOCK™

### --- End of Section ---